## Slide 1
Process Control
Course II
Lecture 10
Optimum Controller Setting

## Slide 2
Optimum Controller Setting
The complexity of high order system makes the selection of controller parameters (Kc, I and R)is difficult. So the controller tuning is often performed using one of the following two methods: Zeigler-Nichols and Cohen-Coon.
1- Ziegler- Nichols Method (Z-N)
This method is also called a closed-loop method. The approach of this method is illustrated in the following steps:
1- Remove the integral and derivative modes of the controller by setting Then the controller becomes proportional.

## Slide 3
2- Select a small value of the proportional gain Kc
3- Disturb the system with a step change.
4- Observe the transient response of the output variable.
5 - If the system decays , then select a higher value of Kc and a gain observe the response of the system
6 - Continue increase the gain Kc in small steps until the response first exhibits sustained oscillation.
0
Tc
t
y

## Slide 4
8 - From The value of the gain Kc and period of oscillation Tc we can predict the optimum values of the controller parameters using Ziegler-Nichols rules as shown in the Table below.
7 - The value of the gain Kc and period of oscillation Tc that correspond to the sustained oscillation are the ultimate gain (Kcmax) and ultimate period of oscillation Tc.
Types of controllers | Gc(s) | Kc | I | R
Proportional P | Kc | 0.5 Kcmax | -- | --
PD | Kc(1+RS) | 0.48 Kcmax | -- | 
PI |  | 0.45 Kcmax |  | --
PID |  | 0.6 Kcmax |  | 
Types of controllers | Gc(s) | Kc | I | R
Proportional P | Kc | 0.5 Kcmax | -- | --
PD | Kc(1+RS) | 0.48 Kcmax | -- | 
PI |  | 0.45 Kcmax |  | --
PID |  | 0.6 Kcmax |  | 

## Slide 5
Example 1
Consider the closed-loop system shown in block diagram below.
∑
+
_
(s)
(s)
)
1- Find the optimum values of the controller parameters (Kc , R and I) using Ziegler-Nichols method.
2- Test the stability.

## Slide 6
Solution
(1). Ziegler-Nichols method
∑
+
_
(s)
(s)
Now, we will use Routh method to find Kcmax

## Slide 7
n
3
2
1
4

## Slide 8
To find ω and Tc

## Slide 9
Using Ziegler – Nichols method
= 0.6(9) = 5.4

## Slide 10
(2). Stability
(s)
∑
+
_
(s)

## Slide 11
n
3
2
1
5
4
The system is stable

## Slide 12
2- Cohen-Coon Method (C-C )
This method is also called reaction curve method or open loop method in which the control action is removed from the controller by placing it in manual mode.
∑
+
+
_
(s)
(s)
M
B
To recorder
Figure 1: splitting the controller from the closed loop.

## Slide 13
Cohen – Coon approach
1- Switch the controller to manual mode. Split the controller from the closed loop.
2- Introduce a step change in the controller output M(s) that goes to the valve and record the transient response (B) as shown in Figure(1)
3- The response of the system (including the valve, the process and the measuring element ) is called the process reaction curve. This response will appear as S-shape as shown in Fig.2
y
0
Time
Fig.2

## Slide 14
4- Draw the horizontal asymptote to the final response KA
y
K A
t
0

## Slide 15
5- locate the inflection point on the response curve f , then draw a tangent to the curve from the inflection point (line ab in the figure below)
y
K A
t
0
b
a

## Slide 16
6- Draw a vertical line from (b) to x-axis and locate point (c) as shown in figure below.
7- From the plot, calculate both; as shown in Figure below.
y
K A
t
0
b
a
c
0

## Slide 17
8- From values of and we can estimate the optimum values of the controller parameters ( Kc, R and I) as shown in the table below.
Types of controllers | Gc(s) | Kc | I | R
Proportional P | Kc |  | -- | --
PD | Kc(1+RS) |  | -- | 
PI |  |  |  | --
PID |  |  |  | 
Types of controllers | Gc(s) | Kc | I | R
Proportional P | Kc |  | -- | --
PD | Kc(1+RS) |  | -- | 
PI |  |  |  | --
PID |  |  |  | 

## Slide 18
Example 2
Consider the closed loop shown below. In order to estimate the optimum values of the controller parameters using Cohen – Coon, A step change of value 7 affect the set point . The controller is set to manual mode and the transient response from the measuring element was recorded . The data is given in the Table below.
1- Plot the data to estimate the optimum parameters of the controller.
2- Test the stability.
Time(min) | 0 | 5 | 10 | 15 | 20 | 25 | 30 | 35 | 40 | 45 | 50 | 55 | 60 | 65 | 70 | 75 | 80 | 85 | 90
Response | 0 | 0.09 | 0.12 | 0.2 | 0.5 | 1 | 2 | 3.2 | 4.2 | 5 | 5.5 | 6 | 6.4 | 6.6 | 6.8 | 6.9 | 6.97 | 6.99 | 7
∑
+
_
(s)
(s)
)

## Slide 19
Solution
1- Set the controller to the manual mode as shown in the Figure below
(s)
_
∑
+
(s)
)
M(s)
B(s)
Step change
Response
(1).

## Slide 20
2- Plot the given data
Chart: Time(min)
| 0 | 5 | 10 | 15 | 20 | 25 | 30 | 35 | 40 | 45 | 50 | 55 | 60 | 65 | 70 | 75 | 80 | 85 | 90
y | 0 | 0.09 | 0.12 | 0.2 | 0.5 | 1 | 2 | 3.2 | 4.2 | 5 | 5.5 | 6 | 6.4 | 6.6 | 6.8 | 6.9 | 6.97 | 6.99 | 7

## Slide 21
2- Plot the tangent and find both
Chart: Time(min)
| 0 | 5 | 10 | 15 | 20 | 25 | 30 | 35 | 40 | 45 | 50 | 55 | 60 | 65 | 70 | 75 | 80 | 85 | 90
y | 0 | 0.09 | 0.12 | 0.2 | 0.5 | 1 | 2 | 3.2 | 4.2 | 5 | 5.5 | 6 | 6.4 | 6.6 | 6.8 | 6.9 | 6.97 | 6.99 | 7
Chart: Time(min)
| 0 | 5 | 10 | 15 | 20 | 25 | 30 | 35 | 40 | 45 | 50 | 55 | 60 | 65 | 70 | 75 | 80 | 85 | 90
y | 0 | 0.09 | 0.12 | 0.2 | 0.5 | 1 | 2 | 3.2 | 4.2 | 5 | 5.5 | 6 | 6.4 | 6.6 | 6.8 | 6.9 | 6.97 | 6.99 | 7

## Slide 22
3- Determine the parameters of the controller as stated by Cohen-Coon

## Slide 23
(2). Stability
n
3
2
1
4
.1
.066
6
The system is stable

## Slide 24
Homework
Q1. Consider the closed-loop system shown in block diagram below. Estimate the optimum value of the controller parameters using Ziegler – Nichol method. Test the stability of the system.
∑
+
_
(s)
(s)
)
Ans:

## Slide 25
Q2. Consider the closed loop shown below. In order to estimate the optimum values of the controller parameters using Cohen – Coon, A step change of value 10 affect the set point . The controller is set to manual mode and the transient response from the measuring element was recorded . The data is given in the Table below.
1- Plot the data to estimate the optimum parameters of the controller(Kc, I and R)
2- Test the stability
∑
+
_
(s)
(s)
)
Time | Response
0 | 0
5 | 0.06
15 | 0.15
25 | 2.1
30 | 5
35 | 8.1
40 | 9.2
45 | 9.5
50 | 9.6
55 | 9.7
60 | 9.8
65 | 9.98
Ans:

## Slide 26
Chart: Time
| 0 | 5 | 15 | 25 | 30 | 35 | 40 | 45 | 50 | 55 | 60 | 65
 | 0 | 0.06 | 0.15 | 2.1 | 5 | 8.1 | 9.2 | 9.5 | 9.6 | 9.7 | 9.8 | 9.98
Homework Q2/ Lecture 10

## Slide 27
Q3. Consider the closed loop shown below. In order to estimate the optimum values of the controller parameters using Cohen – Coon, The controller is set to manual mode. A step change of value 10 is introduced at point M, and the transient response at point B was recorded . The data is given in the Table below.
1- Plot the data to estimate the optimum parameters of the controller(Kc, I and R)
2- Find the value of K
Time | Response
0 | 10
1 | 11
3 | 12
4 | 13
5 | 15
6 | 19
7 | 24
8 | 29
9 | 40
10 | 58
11 | 81
12 | 94
13 | 100
14 | 104
106 | 96
17 | 108
∑
+
_
(s)
(s)
)
M
B

## Slide 28
Chart: t
| 0 | 1 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19
 | 0 | 1 | 2 | 3 | 5 | 9 | 14 | 19 | 30 | 48 | 71 | 84 | 90 | 94 | 96 | 98 | 98 | 98 | 99
τD = 7.8
τ = 12.2 - 7.8 = 4.4

## Slide 29
y(s)
-
+

## Slide 30
Thank you for your attention
Any ?