## Slide 1
Process Control
Course II
Lecture 12
Process Control Loops
Part II
By
Prof. Alaa Kareem Mohammed

## Slide 2
Type of Process Control Loop
1- Feedback Control
2- Feedforward Control
3- Feedforward-plus-Feedback Control
4- Ratio Control
5- Cascade Control
6- Split Range Control

## Slide 3
1- Feedback Control
m Ti
Steam in
m ,To
M
Q
Set point
T E
T T
TI
TRC
Process: Heating tank CSTH
Controlled variable : To
Manipulating variable: Q:

## Slide 4
A feedback loop measures a process variable and sends the measurement to a controller for comparison to set point. If the process variable is not at set point, control action is taken to return the process variable to set point. This control scheme does not take into consideration any of the other variables in the process
Advantages :
1- One of the simplest process control schemes.
2- It is commonly used in the process control industry.
3- It is that directly controls the desired process variable
The disadvantage of feedback loops is that it takes some time in order that the controlled variable reaches the set point.
Disadvantage :

## Slide 5
Example 1
Consider the liquid level tank shown below. Draw a feedback control loop to control the liquid level inside the tank (h). The control loop should contains the following :
h
1- Measuring element
2- Transmitter.
3- Indicator (function in DCS)
4- Recording controlling (front mounted in remote panel)
5- Pneumatic control valve.
6- Give tag No. for these items

## Slide 6
Solution
h
LE
LT
LI
LRC
Set point

## Slide 7
Homework 1
Consider the heating tank system below.
Construct two feedback control loops on the system according to the following description:
First control loop:
Controlled variable : To
Manipulating variable : Q
Second control loop:
Controlled variable : h
Manipulating variable : m
m Ti
Steam in
m ,To
Q
h

## Slide 8
2- Feedforward Control
Feedforward loop is a control system that anticipates load disturbances and controls them before they can impact the process variable. For feedforward control to work, the user must have a mathematical understanding of how the manipulated variables will impact the process variable.
m Ti
Steam in
m ,To
Q
h
For the heating tank shown beside, we notice that
In feedforward control, the controlled variable will be controlled through the load variables only

## Slide 9
Ti
Steam in
m ,To
Q
h
m
F E
F T
FIC
T E
T T
TIC
Set point
Set point

## Slide 10
An advantage of feedforward control is that error is prevented, rather than corrected. Feedforward scheme is better than feedback control scheme in that it takes no time to manipulate the controlled variable when the system is subjected to a disturbance. The difficulty that face the feedforward loop is that it should take into account all the possible load disturbances in a system , but this is either difficult or costly.

## Slide 11
Example 2
h
Consider the liquid level tank shown below. Draw a feedforward control loop to control the liquid level inside the tank (h). Knowing that . The control loop should contains the following :
1- Measuring element
2- Transmitter.
3- Indicator rear mounted on local panel.
4- Recording controlling (field mounted)
5- Pneumatic control valve.

## Slide 12
Solution
h
FE
FT
FRC
FI
Set point

## Slide 13
Example 3
The diagram below shows pH adjustment.
We want to keep the solution in the tank TK-100 at pH=7. The pH of the inlet solution is 5. the adjustment is carried out by addition base NaOH. As shown in diagram beside .
1- Draw feedforward control loop to control outlet pH at 7
2- Repeat (1) using feedback loop only.
pH adjustment tank
TK-100
Base tank
TK-101
F1
Inlet solution
outlet solution
F2
NaOH
pH2
pH1
F3

## Slide 14
Solution
1 - Feedforward loop
F2 is manipulating variable
F1 is load variable
pH adjustment tank
TK-100
Base tank
F1
Inlet solution
outlet solution
F2
TK-101
NaOH
pH2
pH1=5
F3
F E
F T
F IC
Set point

## Slide 15
- Feedback loop
pH2
TK-100
Base tank
F1
Inlet solution
outlet solution
F2
TK-101
NaOH
pH1=5
F3
pH E
pH T
pH IC
Set point

## Slide 16
3- Feedforward-plus-Feedback Control
It is a combined system which consists of two loops feedforward and feedback loops. It is used when the controlled variable is function of many variables, so it is difficult to take account for every possible load disturbance. Feedforward is used for the load disturbance which has great effect on controlled variable. Feedback loop is used for controlled variable.
Controller with summing functions are used in these combined systems to total the input from both the feedforward loop and the feedback loop, and send a unified signal to the final control element.

## Slide 17
Example 4
Steam in
Q
h
m2 T2
m3 T3
m1 T1
Consider the heating vessel below . The temperature of the outlet stream T3 is function of many variables
Inlet flowrate m1 is more effective on the controlled variable T3
Use feedforward –pulse - feedback loop to control the temperature of outlet stream T3.

## Slide 18
Solution
Set point
Steam in
m3 ,T3
Q
m1,T1
F E
F T
FIC
T E
T T
TIC
m2 T2
Set point

## Slide 19
Steam in
m3 ,T3
Q
m1,T1
F E
F T
FIC
T E
T T
TIC
m2 T2
Σ
Set point
Set point
Another solution

## Slide 20
h1
h2
R1
qo
q1
q2
TK101
TK102
Homework 2
R2
q3
Two liquid – level tanks are connected in series as shown in Fig. beside.
The liquid level in the second tank h2 is to be controlled.
Construct control loop to control h2 using:
1- Feedforward loop
2- Feedback loop
3- Feedforward-plus-feedback.
q4

## Slide 21
4- Ratio Control
Ratio control is used to ensure that two or
more flows are kept at the same ratio even
if the flows are changing.
Suppose that the required ratio
The function of FY is to multiply
the output of FT by the required ratio
The result is A , this result is used as the set point to the controller FC
A
1 part of acid
F E
F T
F Y
F E
F T
FIC
B
This unit multiplies (B) by the desired ratio; so the output=
A
Ratio set point

## Slide 22
Ratio control is applied in the following cases :
1- Blending two or more flows to produce a mixture with specified composition
2- Blending two or more flows to produce a mixture with specified physical properties.
3- Maintaining correct air and fuel mixture to combustion.
If the physical characteristic of the mixed flow is measured, a PID controller can be used to manipulate the ratio value For example, a measurement of the density, gasoline octane rating, color, or other characteristic could be used to control that characteristic by manipulating the ratio.

## Slide 23
Example 5
P
Overhead drum
Overhead vapor
Reflex to column
Product
R
Use ratio control loop to control the flow of product (P) and the flow of the reflex (R) that outlet from the overhead drum of a distillation column. The ratio is fixed.

## Slide 24
Solution
FT
P
Overhead drum
Overhead vapor
Reflex to column
Product
R
FT
F E
FY
FE
FIC
Condenser
Ratio set point

## Slide 25
Mixer
A
B
C
FT
R
FT
F E
FY1
FE
FIC
FY2
F E
FT
FIC
Ratio
set point
Ratio set point
A:B:C = 1:2:10
Suppose we have three streams A,B and C as shown in Figure below. The ratio of these streams are A:B:C= 1:2:10. Draw a control loop to adjust the mixed stream at the given ratio.
Ratio control for three streams

## Slide 26
Homework 3
Use the Ratio control loop to adjust the ratio of fuel that inlet to the furnace as shown in Figure below.
Fuel
Air
Furnace
A
B
mixer

## Slide 27
5- Cascade Control
Cascade control consists of two loops ; primary loop and secondary loop.
Primary loop is constructed on the variable to be controlled while the secondary loop is constructed on the manipulating variable.
Consider the shell and tube heat exchanger in Fig. beside. Suppose we want to control the outlet temperature T2 at a certain value by manipulating variable mi using cascade control.
mo , to
Steam
Fluid in T1
Fluid out T2
mi, ti
T T
T E
Set point
F T
FIC
T C
Temperature controller primary
Flow controller secondary
27

## Slide 28
Requirements for cascade control:
Secondary loop process dynamics must be at least four times as fast as primary loop process dynamics.
Secondary loop must have influence over the primary loop.
Secondary loop must be measured and controllable.

## Slide 29
Example 6
Use cascade loop to control the level of the liquid inside the Tank in Figure below. Knowing that . Use as manipulating variable. Repeat the solution if we use feedback loop only.
h

## Slide 30
Solution
h
F E
FT
FIC
LE
LI
LRC
LT
Cascade control loop
Set point

## Slide 31
Feedback control loop
h
Set point
LI
LRC
LE
LT

## Slide 32
Cooling water
m kg/s
Product
T
Reactor
Reactants
Homework 3
Figure below shows a jacketed reactor which carries out exothermic reaction. We want to control the reaction temperature T . The manipulating variable is the flowrate of the cooling water to the jacket(m).
1- use cascade control loop only
2- use feedback control loop only
3- use feedforward – pulse- feedback loop.

## Slide 33
5- Split Range Control
Spilt control loop is very common control scheme in which the output of a controller is split to two or more of control valves. In this case , one of the control valve is chosen normally closed and the other is chosen normally open. For example (Figure below)
FIC
FT
Valve A
Valve B
Controller output 0% Valve A fully open and valve B fully closed
Controller output 25% Valve A is 75% open and valve B is 25% open
Controller output 50 % Valve A is 50 % open and valve B is 50 % open
Controller output 75 % Valve A is 25 % open and valve B is 75 % open
Controller output 100 % Valve A is fully closed and valve B is fully open

## Slide 34
Example 7
(pH adjustment tank)
TK-100
Base tank
Acid tank
TK-101
TK-102
F1
Inlet solution
outlet solution
F2
H2SO4
NaOH
The diagram below shows pH adjustment.
We want to keep the solution in the tank TK-100 at pH=6.
Use split range control loop to adjust the value of pH in the tank at 6 with the aid of the acid and base feeding tanks.

## Slide 35
Solution
(pH adjustment tank)
TK-100
Acid tank
TK-101
F1
Inlet solution
outlet solution
F2
H2SO4
Base tank
TK-102
NaOH
pHE
pHT
pHI
pHC
Set point

## Slide 36
Flare
Process unit
Overhead vapor
Reflex to column
P
Overhead accumulator
Homework 4
Use split range control loop to control the pressure inside the overhead accumulator (shown below). When the pressure exceed the desired value , the line to flare will open so the outlet stream is divided into two stream ;one to flare and the other to process unit.

## Slide 37
Reward (2 marks)
Figure below shows a reactor for detergent production. The inlet liquids are in the ratio of A : B: C= 1: 3: 20
Cooling water in
Product (detergent)
T
Reactor
A
B
C
h
Cooling water out
Sulfonic acid
NaOH
Water
Construct a control system that consists of different loops to control the following output variables:
1- The liquid level inside the reactor (h)
2- The temperature (T) of the reaction mixture.
3- Keep the ratio of inlet feeds constant.

## Slide 38
Cooling water in
Product (detergent)
T
Reactor
h
Cooling water out
Sulfonic acid
NaOH
B
A
FE
FI
FRC
FE
FI
FRC
TE
TI
TRC
LE
LT
LIC
Set point
C
Water
FE
FT
FY1
FY2
Ratio set point
Ratio set point
Set point

## Slide 39
1
6
Overhead drum
B (kg/h)
S (kg/h)
P (kg/h)
R (kg/h)
M (kg/h)
condenser
Distillation column
2
Feed, F
h1
h2
B (kg/h)
Feed, F
w (kg/h)
TF
N (kg/h)
LE
FT
TE
TT
LRC
FE
LT
FRC
FE
FT
FY
set point
TIC
Σ
LE
LT
LRC
set point
set point
Ratio set point

## Slide 40
Cooling water in
Product (detergent)
T
Reactor
A
B
C
h
Cooling water out
Sulfonic acid
NaOH
Water
pH
FE
TI
FRC
FE
FI
FRC
pHE
pHT
pHC
Set point
FE
FT
FY1
TE
Ratio set point
FE
FY2
Ratio set point
Σ
LE
LT
LIC
Set point
TIC
Set point

## Slide 41
Thank you
Any ?