## Slide 1
Process Control
Course II
Lecture 4
The Controllers
Part I

## Slide 2
The controller is part of a closed loop system in which a process variable is measured, compared to a set point, and action is taken to correct any deviation from the set point. Figure 1. shows the input and output signals related to the controller
The Controllers
E(s)
P(s)
Fig.1
The input signal is the error (E) which represents the difference between the set point and the measured value of the controlled variable. The controller will manipulate this error signal (multiplying by a constant or integrating or derivation), according to the type of the controller.

## Slide 3
Then the controller will send a manipulating signal P(t) to the final control element(control valve).
Types of controllers
(A). Discontinuous controller (on-off)
(B). Continuous controllers

## Slide 4
(A). Discontinuous controller (on-off)
Discontinuous controllers sometimes called two position controllers or on-off controllers. These types of controllers are normally used when the process variable need no maintained at precise value.
In these controllers, the manipulated variable changes between discrete values.
On-off controller simply drives the manipulated variable from fully closed to fully open depending on the position of the controlled variable relative to the set point.
A common examples of on-off control are the temperature control in a domestic heating system, oven alarm shutdown, refrigerator , Iron, and hot plate.

## Slide 5
Figure 2 shows the error signal, the difference between measured value and the set point, which transmitted to the controller and the controller action which exit from the on-off controller to the final control element.
Controller action
Error signal
0
0
Figure 2

## Slide 6
(b). Continuous controller
The main feature of continuous controllers is that the controlled variable can have any value within controller’s output range
Types of Controllers
Table 1 shows the type and action of different continuous controllers.
Controller | Symbol | Note
Proportional | P | Multiply the error signal by a constant.
Derivative | D | Derive the error signal. (not used alone)
Integral | I | Integrate the error signal. (not used alone)
Proportional- Derivative | PD | Multiply the error signal by a constant and then derive it
Proportional - Integral | PI | Multiply the error signal by a constant and then Integrate it
Proportional – Integral-Derivative | PID | Multiply the error signal by a constant , Integrate and derive it.
E(s)
P(s)

## Slide 7
1- Proportional controller (P)
2- Proportional –Derivative controller(PD)
3-Proportional- integral controller (PI)
4- Proportional-Derivative-Integral controller (PID)
Practically, the controllers can be classified into four types according to their actions:

## Slide 8
1- Proportional Controller (P controller)
Proportional controller is regarded as the simplest type of the controllers. In the proportional controller, the
The input error signal is multiplied by a factor (constant). This factor is Kc which represent the feature of the proportional controller.
E(s)
P(s)
Where:
: Output signal from controller, (Pneumatic , electrical or hydraulic signal).
: Gain or sensitivity
: error signal.
E= Set point – Measured value.

## Slide 9
Proportional band (P.B%)
The term proportion band is commonly used among process control engineers in place of the term gain.
Proportional band P.B (band width) is defined as the error (expressed as a percentage of the total range of measured error ) required to move the final control element from minimum value to maximum value
max
max
النطاق التناسبي
Transfer function of the proportional controller is
Substitute (4) in (2) gives

## Slide 10
If and are taken as percentage of the total change then
= =1
Equation (5) becomes
Example 1
A proportional controller is used to control temperature within the range of 60 to 100 oC. The controller is adjusted so that the output pressure goes from 3 psi (valve fully open) to 15 psi (valve fully closed) as the measured temperature goes from 71 to 75 oC with the set point held constant. Find the controller gain and the proportional band P.B%.
Solution

## Slide 11
The Offset
There are three key parameters in any control loop: controlled variable, manipulating variable and set point. For an example, for an electric water heater, the heated water temperature is the controlled variable, the required hot water temperature (that is set by user) is the set point. Based on the difference between controlled variable and the set point, controller changes(manipulates) the electric flow(Amp) in the heating coil.
Based controller type, a persistent gap (error) may exists between the controlled variable (To) and set point Tsp in spite of the controller action on the manipulated variable. This steady gap is called offset in process control.
m
cp
Ti
Steam in
m
cp
To
M
Q
Tm
Tsp
E
Comparator
Process
Final control element
Temperature measuring element
Controller
Control Valve
P
الحيد

## Slide 12
Mathematically, offset in Regulator closed loop is defined as:
Offset in Servo closed loop is given by:
or
Calculation of offset

## Slide 13
Example 1
Consider the following closed system:
(s)
(s)
s)
(s)
For a unit step change in , find the time constant of the closed loop, the final value of response and the offset. Sketch the response.
Repeat (a) for value of and .
Conclude the effect of the controller gain on the time constant and the offset.
Repeat (a and b) for unit step change in set point.(Homework)

## Slide 14
Solution
  Unit step change in , that means the loop is regulator.
Final value of the response

## Slide 15
offset

## Slide 16
Final value of the response
offset

## Slide 17
Final value of the response
offset

## Slide 18
  c. For the three values of controller gain Kc, the values of and offset are given in Table 2
0.5 | 0.5 | 0.75
1 | 0.285 | 0.428
2 | 0.15 | 0.28
0.5 | 0.5 | 0.75
1 | 0.285 | 0.428
2 | 0.15 | 0.28
Table 2
From Table 2, we can conclude that:
for faster response]
for lower value of offset]

## Slide 19
Thank you for your listening
Any ?